## TCO Inputs
Released under: FreeBSD
Author: Vasileios Kontorinis (bkontorinis@gmail.com)
Date: 05/16/2012
Comments: If you use these models please cite the paper "Managing Distributed UPS Energy for Effective Power Capping in Data Centers", V.Kontorinis et al. ISCA 2012.
Also send an email to bkontorinis@gmail.com so that we can track who is using the models.
Compatibility: Microsoft Excel v.2007, 2010(Windows), 2011(Mac)
Version: 1.0
Description | Inputs |  |  | Estimated Values
Critical capacity (W) | 10000000 |  | Number of Servers | 33300
Average Rack Power (W) | 4000 |  | Number of Servers with oversubscription | 36297
Rack Footage (Sqft) | 30 |  | Servers per Rack | 17
lifetime - DC Depreciation Time (years) | 10 |  | Servers per Rack with oversubscription | 17
PUE | 1.12 |  | Total Racks | 2500
Server Cost ($) | 798 |  | Total Racks with oversubscription | 2500
Server Depreciation Time (years) | 4 |  | Average server power | 231.25
Server Utilization | 45%
Server Peak Power (W) | 300
Server Idle Power (W) | 175
Electricity Cost ($/kWh) | 0.047
Peak Power Cost ($/kW) | 12
Degree of over-subscription (extra servers) | 0%
Level of over-subscription | Rack
Oversubscription Method | Batteries
|  |  |  | TCO | server cost | server peak power | total servers | perf factor | server total perf | perf / TCO | improv perf/TCO
|  |  |  | 218537331.84 | 798 | 300 | 33300 | 1 | 33,300.00 | 1.52E-04 | 1
|  |  |  | 203550741.2 | 1159 | 500 | 20000 | 2 | 40,000.00 | 1.97E-04 | 1.29
| total cost | power supply (W) |  |  |  |  | 1.665 |  | 1.201201201 | 1.29E+00
machine with CPU only | 798 | 300
http://www.newegg.com/Product/Product.aspx?Item=N82E16883103863
machine with CPU + GPU | 1159.99 | 500 | configuration | TCO | server cost | server peak power | total servers | perf factor | server total perf | perf / TCO | improv perf/TCO | improv perf
http://www.newegg.com/Product/Product.aspx?Item=N82E16883103853 |  |  | CPU only server | 218537331.84 | 798 | 300 | 33300 | 1 | 33,300.00 | 1.52E-04 | 1 | 1
|  |  | CPU+GPU server | 203550741.2 | 1159 | 500 | 20000 | 1 | 20,000.00 | 9.83E-05 | 0.64 | 0.60
|  |  |  | 203550741.2 | 1159 | 500 | 20000 | 2 | 40,000.00 | 1.97E-04 | 1.29 | 1.20
|  |  |  | 203550741.2 | 1159 | 500 | 20000 | 3 | 60,000.00 | 2.95E-04 | 1.93 | 1.80
|  |  |  | 203550741.2 | 1159 | 500 | 20000 | 4 | 80,000.00 | 3.93E-04 | 2.58 | 2.40
|  |  |  | 203550741.2 | 1159 | 500 | 20000 | 5 | 100,000.00 | 4.91E-04 | 3.22 | 3.00
|  |  |  | 203550741.2 | 1159 | 500 | 20000 | 6 | 120,000.00 | 5.90E-04 | 3.87 | 3.60
|  |  |  | 203550741.2 | 1159 | 500 | 20000 | 7 | 140,000.00 | 6.88E-04 | 4.51 | 4.20
|  |  |  | 203550741.2 | 1159 | 500 | 20000 | 8 | 160,000.00 | 7.86E-04 | 5.16 | 4.80
|  |  |  | 203550741.2 | 1159 | 500 | 20000 | 9 | 180,000.00 | 8.84E-04 | 5.80 | 5.41
|  |  |  | 203550741.2 | 1159 | 500 | 20000 | 10 | 200,000.00 | 9.83E-04 | 6.45 | 6.01
Note on A10: IT required power Renge: 100K-30MW
Note on A11: Determines number of racks Range: 2K - 6K
Note on A12: Range: 10-60 Sqft
Note on D12: We assume 20, 2u servers max per rack
Note on A13: Linear depreciation Range:6-15 years
Note on A14: Power Usage Effectiveness Range: 1.0-5.0
Note on A15: Range: > 0
Note on A16: Linear depreciation Range: 1-15
Note on A17: Average server utilization (Affects Oversubscription with batteries tab) Range: 0-1.0
Note on A18: Peak measurable (not nameplate) Range: > Server Idle Power
Note on A19: Idle server power Range: > 0
Note on A20: Range: 0-1.0 ($/kWh) Default based on Duke utility contract. [http://www.duke-energy.com/pdfs/scscheduleopt.pdf]
Note on A21: Range: >= 0 Premium based on peak sustained power for 30mins over the course of a month
Note on A22: Percentage of extra servers accomodated under same power infrastructure. See TCO output tab for associated savings. To estimate a reasonable number using batteries see Oversubscription with batteries tab. Range: 0-50%
Note on A23: Oversubsription at lower power levels is more beneficial. Pdu level oversubscription includes extra rack costs. Cluster level oversubscription includes extra PDU and rack costs.
Note on A24: Battery oversubscription includes increase in UPS cost. Other does not include any additional cost (free)

## TCO Advanced Inputs
Legend
per watt
per Sqft
per Rack
Materials | Mat_
Labor | Lab_
Engineering | Eng_
| Cost per (Watt/Sqft/rack) | Oversubscription scaling | Oversubscription Factor |  | TCO($) | TCO with oversubscription($)
Mat_UPS_perWatt | 0.23 | Scales with Critical capacity | 1 |  | $2,300,000 | $2,300,000
Mat_Battery_perWatt | 0.15 | Scales with Critical capacity | 1 |  | $1,500,000 | $1,500,000
Lab_UPSBattery_perWatt | 0.1 | Scales with Critical capacity | 1 |  | $1,000,000 | $1,000,000
Eng_UPS_perWatt | 0.2 | Scales with Critical capacity | 1 |  | $2,000,000 | $2,000,000
Mat_Generator_perWatt | 0.45 | Scales with Critical capacity | 1 |  | $12,150,000 | $12,150,000
Eng_Generator_perWatt | 0.07 | Scales with Critical capacity | 1 |  | $1,890,000 | $1,890,000
Lab_Generator_perWatt | 0.1 | Scales with Critical capacity | 1 |  | $2,700,000 | $2,700,000
Mat_BackRoomSwitchGear_perWatt | 0.23 | Scales with Critical capacity | 1 |  | $2,300,000 | $2,300,000
Lab_BackRoomSwitchGear_perWatt | 0.1 | Scales with Critical capacity | 1 |  | $1,000,000 | $1,000,000
Eng_BackRoomSwitchGear_perWatt | 0.08 | Scales with Critical capacity | 1 |  | $800,000 | $800,000
Mat_PowerDistributionUnits_perWatt | 0.2 | Scales with Critical capacity | 1 |  | $2,000,000 | $2,000,000
Lab_PowerDistributionUnits_perWatt | 0.1 | Scales with Critical capacity | 1 |  | $1,000,000 | $1,000,000
Eng_PowerDistributionUnits_perWatt | 0.14 | Scales with Critical capacity | 1 |  | $1,400,000 | $1,400,000
Mat_Cooling_perWatt | 0.7 | Scales with Critical capacity | 1 |  | $8,400,000 | $8,400,000
Lab_Cooling_perWatt | 0.4 | Scales with Critical capacity | 1 |  | $4,800,000 | $4,800,000
Eng_Cooling_perWatt | 0.15 | Scales with Critical capacity | 1 |  | $1,800,000 | $1,800,000
Mat_FireDetectionSuppression_perSqft | 40 | Scales with Critical capacity | 1 |  | $3,000,000 | $3,000,000
Lab_FireDetectionSuppression_perSqft | 10 | Scales with Critical capacity | 1 |  | $750,000 | $750,000
Eng_FireDetectionSuppression_perSqft | 4 | Scales with Critical capacity | 1 |  | $300,000 | $300,000
Mat_RaisedFloor_perSqft | 15 | Scales with Critical capacity | 1 |  | $1,125,000 | $1,125,000
Lab_RaisedFloor_perSqft | 15 | Scales with Critical capacity | 1 |  | $1,125,000 | $1,125,000
Eng_RaisedFloor_perSqft | 7 | Scales with Critical capacity | 1 |  | $525,000 | $525,000
Eng_GeneralBuilding_perSqft | 15 | Scales with Critical capacity | 1 |  | $1,125,000 | $1,125,000
Mat_RackEnclosure_perRack | 2000 | Scales with Critical capacity | 1 |  | $5,000,000 | $5,000,000
Mat_RackPowerDistributionWhips_perRack | 800 | Scales with Critical capacity | 1 |  | $2,000,000 | $2,000,000
Lab_RackPowerDistributionWhips_perRack | 200 | Scales with Critical capacity | 1 |  | $500,000 | $500,000
Mat_RackDataCable_perRack | 75 | Scales with Critical capacity | 1 |  | $187,500 | $187,500
Lab_RackDataCable_perRack | 125 | Scales with Critical capacity | 1 |  | $312,500 | $312,500
Mat_SystemMonitoringCost_perSqft | 6.75 | Scales with Critical capacity | 1 |  | $506,250 | $506,250
Mat_InternalExternalProjectMgmt_perSqft | 26 | Scales with Critical capacity | 1 |  | $1,950,000 | $1,950,000
Mat_SpaceLeasing_perSqft | 10 | Scales with Critical capacity | 1 |  | $7,500,000 | $7,500,000
Mat_RaisedFloorCleaning_perSqft | 1 | Scales with Critical capacity | 1 |  | $750,000 | $750,000
Mat_RoomCleaning_perSqft | 0.75 | Scales with Critical capacity | 1 |  | $562,500 | $562,500
Mat_CoolingService_perWatt | 0.09 | Scales with Critical capacity | 1 |  | $10,800,000 | $10,800,000
Mat_UPSBatteryService_perWatt | 0.05 | Scales with Critical capacity | 1 |  | $5,000,000 | $5,000,000
Mat_GeneratorService_perWatt | 0.02 | Scales with Critical capacity | 1 |  | $5,400,000 | $5,400,000
Mat_AncillaryService_perWatt | 0.015 | Scales with Critical capacity | 1 |  | $1,500,000 | $1,500,000
Mat_PowerDistributionUnitsService_perWatt | 0.01 | Scales with Critical capacity | 1 |  | $1,000,000 | $1,000,000
Lighting_WattsperSqft | 2 | Scales with Critical capacity | 1 |  | $609,120 | $609,120
Electrical Substation Cost |  | Scales with Critical capacity | 1 |  | $1,860,000 | $1,860,000
CracSizingvsLoad | 1.2 |  |  | Total | $100,427,870
GeneratorSizingvsLoad | 2.7
Costs grouped according to how they scale
per watt | $70,740,000
per sqft | $19,218,750
per rack | $8,000,000
lighting | $609,120
Note on B11: All these values are extracted from the the Advanced Inputs of the APC online TCO calculator, for the "Legacy System". For more info see http://www.apc.com/tools/isx/tco/
Note on D11: This factors change according to the level of oversubscription. Can be set manually, according to the assumptions of oversubscription
Note on A12: This is the centralized UPS cost. We ignore it since we focus on distributed UPS.
Note on A60: Gets discrete values according to critical capacity crit.cap < 1MW --> cost = 0 1MW < crit.cap < 20MW --> cost = 1.86M $ 20MW < crit.cap --> cost = 2.01M $ Estimated for a 115kV -> 12.5 kV converting substation. [Electric Power Substation Capital Costs, www.osti.gov/bridge/product.biblio.jsp?osti_id=645480]

## TCO Outputs
Total Cost of Ownership NO Oversubscription (Distributed LA UPS) |  |  |  |  | Total Cost of Ownership WITH Oversubscription
| TCO | TCO/Month | TCO/Month/server | Trend with server oversubscription |  | TCO oversub. | TCO/Month | TCO/Month/server
Facility Space | $11,625,000 | $96,875 | $2.91 | Decreasing | Facility Space | $11,625,000.00 | $96,875 | $2.67
UPS | $532,800 | $4,440 | $0.13 | Constant | UPS LFP | 456000 | $3,800 | $0.10
Power Infrastructure | $20,310,000 | $169,250 | $5.08 | Decreasing | Power Infrastructure | $20,310,000.00 | $169,250 | $4.66
Cooling Infrastructure | $8,400,000 | $70,000 | $2.10 | Decreasing | Cooling Infrastructure w PCM | $8,700,000.00 | $72,500 | $2.00
Rest | $30,671,250 | $255,594 | $7.68 | Decreasing | Rest | $30,671,250.00 | $255,594 | $7.04
DC opex | $25,621,620 | $213,514 | $6.41 | Decreasing | DC opex | $25,621,620.00 | $213,514 | $5.88
Server Depreciation | $66,433,500 | $553,613 | $16.63 | Constant | Server Depreciation | $72,412,515.00 | $603,438 | $16.63
Server Opex | $3,321,675 | $27,681 | $0.83 | Constant | Server Opex | $3,620,625.75 | $30,172 | $0.83
PUE overhead | $5,530,874 | $46,091 | $1.38 | Constant | PUE overhead | $5,633,508.55 | $46,946 | $1.29
Utility Energy | $31,705,013 | $264,208 | $7.93 | Constant | Utility Energy | $34,558,464.44 | $287,987 | $7.93
Utility Peak | $14,385,600 | $119,880 | $3.60 | Decreasing | Utility Peak | $14,385,600.00 | $119,880 | $3.30
total | $218,537,332 | $1,821,144 | $54.69 |  | total | $227,994,584 | $1,899,955 | $52.34
[7 empty] | Savings | 4.29%
| Relative TCO Breakdown |  | Relative TCO/server Breakdown |  |  | Relative Breakdown |  | Relative TCO/server Breakdown
Facility Space | 5.32% |  | 5.32% |  | Facility Space | 5.32% |  | 4.88%
UPS | 0.24% |  | 0.24% |  | UPS | 0.21% |  | 0.19%
Power Infrastructure | 9.29% |  | 9.29% |  | Power Infrastructure | 9.29% |  | 8.53%
Cooling Infrastructure | 3.84% |  | 3.84% |  | Cooling Infrastructure w PCM | 3.98% |  | 3.65%
Rest | 14.03% |  | 14.03% |  | Rest | 14.03% |  | 12.88%
DC opex | 11.72% |  | 11.72% |  | DC opex | 11.72% |  | 10.76%
Server Depreciation | 30.40% |  | 30.40% |  | Server Depreciation | 33.14% |  | 30.40%
Server Opex | 1.52% |  | 1.52% |  | Server Opex | 1.66% |  | 1.52%
PUE overhead | 2.53% |  | 2.53% |  | PUE overhead | 2.58% |  | 2.36%
Utility Energy | 14.51% |  | 14.51% |  | Utility Energy | 15.81% |  | 14.51%
Utility Peak | 6.58% |  | 6.58% |  | Utility Peak | 6.58% |  | 6.04%
[5 empty] | Savings | -4.33% |  | 4.29%
total | 100.00% |  | 100.00% |  | total | 104.33% |  | 100.00%
Trend with server oversubscription
Decreasing | 47.24%
Constant | 46.17%
Note on A3: Space cost without CLEAINING
Note on G3: Space cost without CLEAINING
Note on A4: Estimated as the cost of per server lead acid batteries (2$/Ah x 3.2Ah)
Note on G4: Estimated as the cost of per server LFP batteries (5$/Ah x 40 Ah)
Note on A5: Power Infrastructure with Electical Substation cost, without centralized UPS
Note on G5: Power Infrastructure with Electical Substation cost, without centralized UPS
Note on A8: Includes service and lighting
Note on G8: Includes service and lighting
Note on A10: Estimated as 5% of server cost [L.Barroso et al. "The Datacenter as a Computer...", Google book]
Note on G10: Estimated as 5% of server cost [L.Barroso et al. "The Datacenter as a Computer...", Google book]
Note on G18: Space cost without CLEAINING
Note on G19: Estimated as the cost of per server lead acid batteries
Note on G20: Power Infrastructure with Electical Substation cost, without centralized UPS
Note on G23: Includes service and lighting
Note on G25: Estimated as 5% of server cost [L.Barroso et al. "The Datacenter as a Computer...", Google book]

## Oversubscription with batteries
Description | Inputs |  |  |  | Estimated |  |  | Hour | No Shaving | With Shaving
[5 empty] | Battery depr. time (months) | 100.0 |  | 1 | 270.0 | 218.2
Battery Type | LFP |  |  |  | Imax (A) | 20.0 |  | 2 | 270.0 | 218.2
Battery Voltage | 12 | [6 empty] | 3 | 270.0 | 218.2
Sever PSU efficiency | 80% | [6 empty] | 4 | 270.0 | 218.2
[6 empty] | No shaving | With Shaving | 5 | 223.5 | 234.4
Worload Specific |  |  |  |  | High Pulse Height | 270.0 | 218.2 | 6 | 223.5 | 234.4
Peak Pulse Width (h) | 4 |  |  |  | Low Pulse Height | 223.5 | 234.4 | 7 | 223.5 | 234.4
Peak Pulse Height | 90% | [6 empty] | 8 | 223.5 | 234.4
Targeted Peak Reduction | 19.2% |  |  |  | Max Peak Reduction | 14.2% |  | 9 | 223.5 | 234.4
Discharges per day | 1 | [6 empty] | 10 | 223.5 | 234.4
[5 empty] | Required Battery Capacity (Ah) | 32.6 |  | 11 | 223.5 | 234.4
Battery Type Specific |  |  |  |  | UPS cost per server ($) | 163.2 |  | 12 | 223.5 | 234.4
Battery Cost ($/Ah) | 5 |  |  |  | UPS depreciation / month ($) | 1.6 |  | 13 | 223.5 | 234.4
Peukert's exponent | 1.05 |  |  |  | Allowed Oversubscription | 23.8% |  | 14 | 223.5 | 234.4
DoD goal | 60% | [6 empty] | 15 | 223.5 | 234.4
Service life (months) | 120 | [6 empty] | 16 | 223.5 | 234.4
Battery Efficiency | 95% | [6 empty] | 17 | 223.5 | 234.4
[8 empty] | 18 | 223.5 | 234.4
DoD | Rech.cycles | [6 empty] | 19 | 223.5 | 234.4
10% | 100000 | [6 empty] | 20 | 223.5 | 234.4
20% | 40000 | [6 empty] | 21 | 223.5 | 234.4
30% | 10000 | [6 empty] | 22 | 223.5 | 234.4
40% | 6000 | [6 empty] | 23 | 223.5 | 234.4
50% | 4000 | [6 empty] | 24 | 223.5 | 234.4
60% | 3000
70% | 2000
80% | 1700
90% | 1200
100% | 1000
Analysis
Capacity Size Limit (Ah) | 40
Peak Width
| 32.6 | 0.5 | 1 | 2 | 4 | 8 | 16
Targeted Peak Reduction | 5% | 1.4594 | 2.8239 | 5.4645 | 10.5742 | 20.4617 | 39.5947
| 10.0% | 2.8239 | 5.4645 | 10.5742 | 20.4617 | 39.5947 | 76.6182
| 14.2% | 4.1549 | 8.04 | 15.5579 | 30.1056 | 58.2562 | 112.7295
| 14.2% | 5.3182 | 10.291 | 19.9138 | 38.5344 | 74.5665 | 144.291
| 14.2% | 5.3177 | 10.2901 | 19.9119 | 38.5308 | 74.5596 | 144.2776
Note on A8: The graph demonstrates the daily pattern of the load. Power = idle power + utilization * (peak power - idle power) (see TCO inputs sheet)
Note on A11: Must be smaller than Max Peak Reduction
Note on F13: The Ah is estimated based on required discharge energy. We account for discharge properties (peukert's law), DoD and capacity loss throughout lifetime. Finally we scale it to 20h-rating.

## Validation
APC Calculator -- VALIDATION
PowerEQ | $22,250,000
CoolingEQ | $8,400,000
EngInstLab | $23,027,500
Service | $23,700,000
RacksEnclos | $5,187,500
Space | $12,937,500
SysMon | $506,250
ProjMan | $1,950,000
Lighting | $609,120
Total infrastructure costs (no Lighting) | $97,958,750
Infrastructure costs+ Dist.UPS + Substation Cost | $96,231,870
Note on A1: To validate run APC TCO calculator (http://www.apc.com/tools/isx/tco/) with: - Design Power Rating(W): 10,000,000 - Starting Load - % of Design Power: 100 - Ending Load - % of Design Power: 100 - Average Rack Power (Watts/Rack): 4000 - % of Infrastructure Design Life when Ending Load is reached: 100 - Electricity Cost ($/kw-hr): 0.00000000001 (very small to be ignored, we estimate it separately according to utility contract) - The rest are the default values It will complain with 4 alerts, click ok, it is fine... Click the results and select the Infrastructure Cost breakdown "Alternative Report" The "System TCO by Category" should match in all components except for PowerEQ. This is because in the APC calculator they assume an "unknown" non-linear factor that effectively significantly reduces PowerEQ costs for critical capacity > 2MW. We assume that PowerEQ scales linearly. Also note that the centralized UPS components are ignored (replaced by the battery cost of distributed UPS, in the TCO Outputs analysis)
Note on A2: Includes: Power Distribution whips, PDUs, backroomswitch gear, generator, UPS, batteries
Note on A3: Includes: CRAC etc
Note on A4: Includes: enginnering and labor for everything
Note on A6: Includdes: Racks, datacables
Note on A7: Includes Lease, fireprotection, raisedfloor, Cleaning for room and raised floor
Note on A8: Includes only system monitors
Note on A9: Includes: project internal and external management
Note on A10: Includes: Lighting
Note on A15: This is approximately 10$/W of critical capacity for infrastructure costs which is in the correct range based on ["The Datacenter as a Computer", Barosso et al.]

## Utils
Oversubscription Level Options |  |  | License Information:
Rack |  |  | Copyright (c) 2012, Vasileios Kontorinis
PDU |  |  | All rights reserved.
Cluster
Redistribution and use in source and binary forms, with or without modification, are permitted provided that the following conditions are met:
Oversubscription Scaling Options
Scales with Critical capacity |  |  | Redistributions of source code must retain the above copyright notice, this list of conditions and the following disclaimer.
Scales with Server Power |  |  | Redistributions in binary form must reproduce the above copyright notice, this list of conditions and the following disclaimer in the documentation and/or other materials provided with the distribution.
Custom |  |  | THIS SOFTWARE IS PROVIDED BY THE COPYRIGHT HOLDERS AND CONTRIBUTORS "AS IS" AND ANY EXPRESS OR IMPLIED WARRANTIES, INCLUDING, BUT NOT LIMITED TO, THE IMPLIED WARRANTIES OF MERCHANTABILITY AND FITNESS FOR A PARTICULAR PURPOSE ARE DISCLAIMED. IN NO EVENT SHALL THE COPYRIGHT HOLDER OR CONTRIBUTORS BE LIABLE FOR ANY DIRECT, INDIRECT, INCIDENTAL, SPECIAL, EXEMPLARY, OR CONSEQUENTIAL DAMAGES (INCLUDING, BUT NOT LIMITED TO, PROCUREMENT OF SUBSTITUTE GOODS OR SERVICES; LOSS OF USE, DATA, OR PROFITS; OR BUSINESS INTERRUPTION) HOWEVER CAUSED AND ON ANY THEORY OF LIABILITY, WHETHER IN CONTRACT, STRICT LIABILITY, OR TORT (INCLUDING NEGLIGENCE OR OTHERWISE) ARISING IN ANY WAY OUT OF THE USE OF THIS SOFTWARE, EVEN IF ADVISED OF THE POSSIBILITY OF SUCH DAMAGE.
Oversubscription Method
Batteries
Other
Battery Type
LFP
LA
| LFP | LA
Battery Cost ($/Ah) | 5 | 2
Peukert's exponent | 1.05 | 1.15
DoD goal | 60% | 40%
Service life (months) | 120 | 48
Battery Efficiency | 95% | 75%
DoD | LFP rech.cycles | LA rech.cycles
10% | 100000 | 5000
20% | 40000 | 2800
30% | 10000 | 1860
40% | 6000 | 1300
50% | 4000 | 1000
60% | 3000 | 830
70% | 2000 | 650
80% | 1700 | 500
90% | 1200 | 410
100% | 1000 | 330

## Server Power
Inlet Temperature (F) | Power | Inlet Temperature (In Centigrade) | Normzlied Server Power
62.5 | 360 | 17 | 86
66 | 361 | 19 | 86
70 | 363 | 21 | 86
74 | 366 | 23 | 87
77 | 370 | 25 | 88
81 | 378 | 27 | 90
84 | 390 | 29 | 93
88 | 403 | 31 | 96
90 | 420 | 32 | 100
94 | 440 | 34 | 105